Delivering High Availability is much more than just providing a few token HA features in hardware. The entire end-to-end solution must be considered before a system can be labeled as acceptable for mission critical environments.

The ‘HA pyramid’ demonstrates this best.

Each level of the pyramid is nothing without the level below it. For instance, what good is hard partitioning if the system underneath it fails at an unacceptable rate? What good are virtual partitions if you cannot section them off into hard partitions when extra isolation is required? (For example, when HW isolation is desired between a production partition and a development partition.)

What good is any system without a management scheme (system and fault) that doesn’t seamlessly connect and integrate with all servers in a data center?

I will discuss HP’s solutions in these areas, specifically EMS and HAO (high availability observatory). Specific tips / recommendations on configuring these tools will be presented.

# A computer can be divided into 4 basic subsystems:

- CPU

- Memory

- IO

- Cabinet infrastructure

Superdome has HA features that address each of these subsystems. Each has been specifically designed (using field data) to reduce the REAL causes of downtime.

In HP systems, the hardware works in tandem with EMS to cover most system errors. It is estimated that over 90% of all system errors are covered by HA features. (Achieving 100% requires fault tolerant computers.)  It is therefore imperative that EMS is setup and configured correctly.

This portion of the paper will discuss two specific cases in which EMS is an integral part of the solution, then discuss some EMS tricks / tips.

The memory subsystem design is such that a single SDRAM chip does not contribute more than 1 bit to each ECC word. The memory system is built with x4 SDRAMS. Each main memory access results in 576 bits being read, 4 bits each from 144 SDRAMS. The 576 bits are divided into 4 separate ECC domains, with each SDRAM contributing only one bit to each ECC domain. Each ECC domain can correct one bit in error. Therefore, the ONLY way to get a multiple bit memory error from SDRAMS is if more than one SDRAM failed at the same time, which statistically will not occur.

The system is also resilient to any cosmic ray or alpha particle strike because, at the most, these failure modes can only affect multiple bits in a single SDRAM. These types of failures are also avoided with this architecture, again since no SDRAM contributes more than one bit to an ECC domain.  The memory is effectively RAID’d or stripped, similar to high-end disk storage systems. Data is protected!

This scheme is sometimes called ‘chip-kill’ in the industry. ‘Chip-spare’ or ‘dynamic memory resiliency’ are the terms used by HP, since it more accurately portrays the fact that the memory chips can be thought of as being redundant. N+1 per set of 4 DIMMS.

Some in the industry deal with multi-bit SDRAM failures by accepting the fact that they will occur. That is, a scheme is used that supports failure detection, but not correction. This scheme, while it may be acceptable in low-end markets, is a dangerous choice for those customers that are ‘betting their business’ on not having any downtime. Systems based upon this ‘corner cutting’ are at high risk to fail due to memory problem.

Dynamic page de-allocation (DMR) works by ‘sparing-out’ memory pages that have hard single bit errors. This prevents possible data corruption / system crashes due to a cosmic ray event that just happens to occur in the same memory word as the hard error. There are 50 - 200 spare pages available. This compares favorably with other schemes in the industry, which use hardware based schemes that are costly and are limited by the number of spares DRAMS.

Further aiding in this process is the ‘HW memory scrubber’, which automatically corrects and clears single-bit errors in every memory line that is read by the CPUs. This is an advantage over most SW based scrubbers, which are limited to ‘scrubbing’ only that memory which is not ‘locked down’ by the OS or an application. In competitive systems, a single bit memory error can be a ticking time bomb that can blow if a subsequent single bit memory error occurs in the same memory rank.

Fault Management provides immediate alerts of potential problems, as well as real problems as soon as they are detected.  Customers are then able to take corrective action.  In some cases fault monitors are smart enough to repair or prevent future faults from occurring.  Fault Management currently uses the EMS (Event Management System) infrastructure for its notification methodology. EMS enables a wide variety of notification methods (pager, email, SNMP traps, system console, system log, text logfile TCP/UDP, OpenView OPC messaging).

Fault Management events can themselves be viewed and browsed directly by the customer on the actual system, or the customer can install HP’s TopTools Management server and aggregate information from multiple systems in the data center.

Customers also have the option to integrate Fault Management events with Enterprise Management software like HP’s OpenView or other Enterprise Management software from BMC, Tivoli, Computer Associates or MicroMuse.

The typical hardware monitoring process works as follows:

- While monitoring its hardware resources, the hardware event monitor detects some type of abnormal behavior on one of the resources.

- The hardware event monitor creates the appropriate event message, which includes suggested corrective action, and passes it to the Event Monitoring Service (EMS).

- EMS sends the event message to the system administrator using the notification method specified in the monitoring request.

- The system administrator (or Hewlett-Packard service provider) receives the messages, corrects the problem, and returns the hardware to its normal operating condition.

If the Peripheral Status Monitor (PSM) has been properly configured, events are also processed by the PSM. The PSM changes the device status to DOWN if the event is serious enough. The change in device status is passed to EMS, which in turn alerts MC/ServiceGuard. The DOWN status will cause MC/ServiceGuard to failover any package associated with the failed hardware resource.

Example of Adding a Monitoring Request

The following example illustrates the process of adding a monitoring request. In this example a request is

added that will send all CRITICAL events detected by the AutoRAID disk array monitor to an email address of admin@hp.com.

===================================================================

=========== Monitoring Configuration Main Menu =============

Select:

(S)how current monitoring requests configured via monconfig

(C)heck detailed monitoring status

(L)ist descriptions of available monitors

(A)dd a monitoring request

(D)elete a monitoring request

(M)odify an existing monitoring request

(E)nable Monitoring

(K)ill (disable) monitoring

(H)elp

(Q)uit

Enter selection: [s] a <== SELECT ADD OPTION

===========================================================================

===================== Add Monitoring Request =====================

Start of edit configuration:

A monitoring request consists of:

- A list of monitors to which it applies

- A severity range (A relational expression and a severity. For example,

%< "MAJOR WARNING" means events with a severity "INFORMATION" and

"MINOR WARNING")

- A notification method

Please answer the following questions to specify a monitoring request.

Monitors to which this configuration can apply:

1) /storage/events/disk_arrays/AutoRAID

2) /storage/events/disks/default

3) /adapters/events/FC_adapter

4) /connectivity/events/multiplexors/FC_SCSI_mux

5) /storage/events/enclosures/ses_enclosure

6) /storage/events/tapes/SCSI_tape

7) /storage/events/disk_arrays/FW_SCSI

8) /storage/events/disk_arrays/High_Availability

Enter monitor numbers separated by commas

{or (A)ll monitors, (Q)uit, (H)elp} [a] 1 <== SELECT AUTORAID MONITOR

Criteria Thresholds:

1) Informational 2) Minor Warning 3) Major Warning

4) Serious 5) Critical

Enter selection {or (Q)uit,(H)elp} [4] 5 <== SELECT ONLY CRITICAL EVENTS

Criteria Operator:

1) %< 2) %<= 3) > 4) >= 5) = 6) !

Enter selection {or (Q)uit,(H)elp} [4] 5 <== (=CRITICAL)

Notification Method:

1) UDP 2) TCP 3) OPC 4) SNMP

5) TEXTLOG 6) SYSLOG 7) EMAIL 8) CONSOLE

Enter selection {or (Q)uit,(H)elp} [7] <== SELECT EMAIL ADDRESS

Enter Email Address: [root] admin@hp.com admin@hp.com

User Comment:

(C)lear (A)dd

Enter selection {or (Q)uit,(H)elp} [c] a <== ADD COMMENT

Enter comment: [] This is a test message. IF DESIRED

Client Configuration File:

(C)lear (A)dd

Use Clear to use the default file.

Enter selection {or (Q)uit,(H)elp} [c] c <== SPECIFY CLCFG FILE IF DESIRED (USUALLY

CHOOSE DEFAULT)

New entry:

Send events generated by all monitors

/storage/events/disk_arrays/AutoRAID <== NEW MONITORING with severity = CRITICAL to EMAIL admin@hp.com REQUEST with comment: “This is a test message”

Are you sure you want to keep these changes?

{(Y)es,(N)o,(H)elp} [n] y

Modifying Monitoring Requests

Modifying an existing monitoring request is a convenient way to alter one of the settings used in the request. Simply select a monitoring request and then change the desired setting. All other aspects of the request remain unchanged.

To modify a monitoring request:

1. Run the Hardware Monitoring Request Manager by typing:

/etc/opt/resmon/lbin/monconfig

2. From the main menu selection prompt, enter M

All current monitoring requests are displayed.

3. From the list of current monitoring requests, enter the number of the request you want to modify.

4. As you are prompted for each monitoring request setting, change the settings to achieve the desired results.

5. Save the request when prompted.

Retrieving and Interpreting Event Messages

Event messages generated by hardware monitoring can be delivered using a variety of notification methods.

To simplify receiving event messages you may want to use the email and/or textfile notification methods.

Both of these methods, which are included in the default monitoring, receive the entire content of the message so you can read it immediately.

Methods such as console, syslog, and SNMP alert you to the occurrence of an event but do not deliver the

entire message. You are required to retrieve it using the resdata utility. For these methods, the event

notification will include a message similar to the following:

Execute the following command to obtain event details: /opt/resmon/bin/resdata

-R 392036357 -r /storage/events/tapes/SCSI_tape/10_12_5.0.0 -n 392036353 -a

It is important that you execute the command exactly as indicated, including the two critical number fields that are indexes for the resdata entries.

Sample Event Message

The following is a portion of a sample event message:

> Event Monitoring Service Event Notification %<

Notification Time: Wed Sep 9 10:48:30 1998

hpbs8684 sent Event Monitor notification information:

/storage/events/disks/default/10_4_4.0.0 is >= 1.

Its current value is CRITICAL(5).

Event data from monitor:

Event Time : Wed Sep 9 10:48:30 1998

Hostname : hpbs8684.boi.hp.com IP Address : 15.62.120.25

Event Id : 0x0035f6b15e00000000 Monitor : disk_em

Event # : 100037 Event Class : I/O

Severity : CRITICAL

Disk at hardware path 10/4/4.0.0 : Media failure

Associated OS error log entry id(s):

000000000000000000

Description of Error:

The device was unsuccessful in reading data for the current I/O request due to an error on the medium. The data could not be recovered. The request was likely processed in a way which could cause damage to or loss of data.

Probable Cause / Recommended Action:

The medium in the device is flawed. If the medium is removable, replace

the medium with a fresh one. Alternatively, if the medium is not

removable, the device has experienced a hardware failure.

Repair or replace the device, as necessary.

Tips for Hardware Monitoring

Here are some tips for using hardware monitoring.

Keep hardware monitoring enabled to protect your system from undetected failures. Hardware monitoring is an important tool for maintaining high-availability on your system. In a high-availability environment, the failure of a hardware resource makes the system vulnerable to another failure. Until the failed hardware is repaired, the backup hardware resource represents a single-point of failure. Without hardware monitoring you may not be aware of the failure. But if you are using hardware monitoring, you are alerted to the failure. This allows you to repair the failure and restore high-availability as quickly as possible.

Integrate the peripheral status monitor (PSM) into your MC/ServiceGuard strategy. An important feature of hardware monitoring is its ability to communicate with applications responsible for maintaining system availability, such as MC/ServiceGuard. The peripheral status monitor (PSM) allows you to integrate hardware monitoring into MC/ServiceGuard. The PSM gives you the ability to failover a package based on an event detected by hardware monitoring. If you are using MC/ServiceGuard, you should consider using the PSM to include your system hardware resources in the MC/ServiceGuard strategy. In addition, the necessary notification methods are provided for communicating with network management application such as HP OpenView.

Utilize the many notification methods available. The notification methods provided by hardware monitoring provide a great deal of flexibility in designing a strategy to keep you informed of how well your system hardware is working. The default monitoring configuration was selected to provide a variety of notification for all supported hardware resources. As you become familiar with hardware monitoring, you may want to customize the monitoring to meet your individual requirements.

Use email and/or textfile notification methods for all your requests. Both of these methods, which are included in the default monitoring, receive the entire content of the message so you can read it immediately. Methods such as console and syslog alert you to the occurrence of an event but do not deliver the entire message. You are required to retrieve the message using the resdata utility, which requires an additional step.

Use the `All monitors' option when creating a monitoring request. This applies the monitoring request to all monitors. This has the benefit of ensuring a new class of hardware resource added to your system will automatically be monitored. This means thatnew hardware is protected from undetected hardware failure with no effort on your part.

Easily replicate your hardware monitoring on all your systems. Once you have implemented a hardware monitoring strategy on one of your system, you can replicate that same monitoring on other systems. Simply copy all of the hardware monitor configuration files to each system that will use the same monitoring. The monitor configuration files live in /var/stm/config/tools/monitor. Of course, you must have installed hardware event monitoring on each system before you copy the configuration files to it. Be sure to enable monitoring on all systems.

Each hard partition runs its own independent instance of the operating system. Applications cannot span hard partitions since each partition runs its own instance of the OS, essentially functioning as a stand-alone server.  However, different partitions may be executing the same or different revisions of an operating system, or they may be executing different operating systems altogether . (In later versions of hard partitions).

Unlike other systems with domains, HP’s hard partitions have hardware dedicated to ‘guarding’ partitions from errant transactions generated on failing partitions. A failure in one domain will not affect any other domains

These features result in a much lower shared failure (Single points of failure) rate between hard partitions than in other systems.

Par-Manager is the tool that is used to setup and configure hard partitions.

- The HAO helps HP provide fast, dependable proactive and reactive support services, which reduces costly downtime in your mission critical environment

- The HAO significantly reduces unplanned downtime by providing critical information on systems and network inter-connect devices to HP more quickly

- The HAO helps you to increase the productivity of your network, systems and applications to yield a higher return on your IT investments

The HAO raises system availability by proactively addressing potential problem areas

• A collection is a snapshot of configuration data for the specified devices. Although a collection generates only one set of data, it can take from a few seconds to a few hours to build this snapshot.

• The Time1 timestamp that appears above the Tracking Tree denotes the time that the Time1 collection began. The Time2 timestamp denotes the time that the Time2 collection ended.

• The timeframe is from the beginning of Time1 to the end of Time2.

• Application Patch Analyzers analyze systems and recommend patches based on a specific HP-UX application or group of HP-UX products.

• Use known Good Models (KGMs) to compare against customer configuration information

• Generate cases in Clarify (WFM) and report differences

• Review patch summary reports using MCSC Monitor

1. When an event occurs, the Agent process creates an event file in .ser format. It then converts that file into .txt format so Tracker can collect it. (The .txt version is deleted after each collection.)

2. The Tracker Collector pulls only new event data from the client via the rpc protocol during a Tracker collection using the HA Meter collectible. The data is then stored in the Tracker database and sent to the HA Meter post-processor, where it is converted back into the .ser format so the Server process can read it.

3. Event data in the Tracker database is viewable via the Tracker UI. Event data in the Server process can appear in Availability Reports on the HPSN (for ASEs) and in customer reports via the CA Server at the MCSC using HA Reporter on your workstation.

Availability Report for 'Valued HP Customer'                                                                                  Page 1

From Wed Dec 31 17:00:00 MST 1969 (HA Meter installation) to Thu Sep 27 14:57:12 MDT 2001.

Printed on Thu Sep 27 14:57:12 MDT 2001 at lonewolf.fc.hp.com

HAMeter revision A.02.50.003

************************************************************************************************************************************

===================================================  HP-UX System Event History  ===================================================

Event Date                               Entity                     Class     Downtime     +? P? Notes

===== ================================== ========================== ========= ============ == == ================================

1 Tue Aug 14 18:33:27 CEST 2001      ares.olympus.hp.com        system                       Began measurement.

2 Tue Aug 14 18:33:47 CEST 2001      zeus.olympus.hp.com        system                       Began measurement.

3 Tue Aug 14 18:37:05 CEST 2001      apollo.olympus.hp.com      system                 +     Began measurement.

4 Wed Aug 15 06:30:07 CEST 2001      ares.olympus.hp.com        system            2480     N went down

5 Thu Aug 16 19:03:51 CEST 2001      zeus.olympus.hp.com        system           33509     N went down

6 Sun Aug 19 21:36:47 CEST 2001      ares.olympus.hp.com        system            5784     N went down

7 Thu Aug 23 13:19:35 MDT 2001       athena.olympus.hp.com      system                       Measurement terminated.

8 Thu Aug 23 13:23:13 MDT 2001       athena.olympus.hp.com      system                       Began measurement.

9 Thu Aug 23 13:42:38 MDT 2001       hermes.olympus.hp.com      system                       Measurement terminated.

10 Thu Aug 23 13:44:16 MDT 2001       hermes.olympus.hp.com      system                       Began measurement.

11 Thu Sep 27 13:41:28 MDT 2001       hermes.olympus.hp.com      system               6     N went down

12 Thu Sep 27 13:45:17 MDT 2001       athena.olympus.hp.com      system              12     Y halted: 6

===== ================================== ========================== ========= ============ == == ================================

All times in minutes.  See note at end about rounding.                              + = event ongoing at end of reporting period.

************************************************************************************************************************************

===========================================  Aggregate HP-UX System Availability Report  ===========================================

Number of downtime events:                      5

Number of planned downtime events:           1

Number of unplanned downtime events:         4

Aggregate measurement time:                 291835

Total downtime:                             41790

Total planned downtime:                     12

Total unplanned downtime:                41778

HP-UX System availability for the period:   85.680%

************************************************************************************************************************************

===========================================  Detailed HP-UX System Availability Report  ============================================

Entity                   Accuracy     Entity info                                                  Availability R?

======================== ============ ============================================================ ============ ==

apollo.olympus.hp.com    +/- 0.5  min 9000/871  500776557 HP-UX B.11.11                                100.000%

ares.olympus.hp.com      +/- 0.5  min 9000/889  529186261 HP-UX B.11.00                                 87.012%

athena.olympus.hp.com    +/- 0.5  min 9000/871  2006045407 HP-UX B.10.20                                99.976%

hermes.olympus.hp.com    +/- 0.5  min 9000/871  2003231967 HP-UX B.10.20                                99.989%

zeus.olympus.hp.com      +/- 0.5  min 9000/800  524786597 HP-UX B.11.11                                 47.332%

************************************************************************************************************************************

=============================================  MC/ServiceGuard Cluster Event History  ==============================================

Event Date                               Entity                     Class     Downtime     +? P? Notes

===== ================================== ========================== ========= ============ == == ================================

1 Fri Aug 17 00:06:40 CEST 2001      webserver                  cluster                      Began measurement.

2 Fri Aug 17 00:20:40 CEST 2001      webserver                  cluster                      Measurement terminated.

3 Fri Aug 17 00:32:22 CEST 2001      webserver                  cluster                +     Began measurement.

4 Thu Aug 23 13:30:10 MDT 2001       cluster10                  cluster                      Began measurement.

5 Thu Aug 30 17:17:40 MDT 2001       cluster10                  cluster              1       Down

6 Thu Sep 27 13:45:17 MDT 2001       cluster10                  cluster             72 +     Down

===== ================================== ========================== ========= ============ == == ================================

All times in minutes.  See note at end about rounding.                              + = event ongoing at end of reporting period.

************************************************************************************************************************************

=====================================  Aggregate MC/ServiceGuard Cluster Availability Report  ======================================

Number of downtime events:                      2

Aggregate measurement time:                 110886

Total downtime:                                73

MC/ServiceGuard Cluster availability for the period:   99.934%

************************************************************************************************************************************

======================================  Detailed MC/ServiceGuard Cluster Availability Report  ======================================

Entity                   Accuracy     Entity info                                                  Availability R?

======================== ============ ============================================================ ============ ==

cluster10                +/- 0.5  min MC/ServiceGuard A.10.12 2006045407 EMS HA Monitors A.03.20        99.856%

webserver                +/- 0.5  min MC/ServiceGuard A.11.09 524786597 EMS HA Monitors A.03.20.01     100.000%

************************************************************************************************************************************

============================================  MC/ServiceGuard Localnode Event History  =============================================

Event Date                               Entity                     Class     Downtime     +? P? Notes

===== ================================== ========================== ========= ============ == == ================================

1 Fri Aug 17 00:06:40 CEST 2001      webserver/apollo           localnode                    Began measurement.

2 Fri Aug 17 00:06:46 CEST 2001      webserver/zeus             localnode                    Began measurement.

3 Fri Aug 17 00:20:40 CEST 2001      webserver/apollo           localnode                    Measurement terminated.

4 Fri Aug 17 00:20:46 CEST 2001      webserver/zeus             localnode                    Measurement terminated.

5 Fri Aug 17 00:32:22 CEST 2001      webserver/apollo           localnode              +     Began measurement.

6 Fri Aug 17 00:32:28 CEST 2001      webserver/zeus             localnode              +     Began measurement.

7 Thu Aug 23 13:30:10 MDT 2001       cluster10/athena           localnode                    Began measurement.

8 Thu Aug 23 13:45:38 MDT 2001       cluster10/hermes           localnode                    Began measurement.

9 Thu Aug 30 15:39:42 MDT 2001       cluster10/athena           localnode           52       Down

10 Thu Aug 30 17:00:41 MDT 2001       cluster10/athena           localnode           18       Down

11 Thu Aug 30 17:17:40 MDT 2001       cluster10/hermes           localnode            1       Down

12 Thu Aug 30 17:44:41 MDT 2001       cluster10/athena           localnode            3       Down

13 Thu Sep 27 13:41:28 MDT 2001       cluster10/hermes           localnode           76 +     Down

14 Thu Sep 27 13:45:17 MDT 2001       cluster10/athena           localnode           72 +     Down

===== ================================== ========================== ========= ============ == == ================================

All times in minutes.  See note at end about rounding.                              + = event ongoing at end of reporting period.

************************************************************************************************************************************

====================================  Aggregate MC/ServiceGuard Localnode Availability Report  =====================================

Number of downtime events:                      6

Aggregate measurement time:                 221757

Total downtime:                               220

MC/ServiceGuard Localnode availability for the period:   99.900%

************************************************************************************************************************************

=====================================  Detailed MC/ServiceGuard Localnode Availability Report  =====================================

Entity                   Accuracy     Entity info                                                  Availability R?

======================== ============ ============================================================ ============ ==

cluster10/athena         +/- 0.5  min MC/ServiceGuard A.10.12 2006045407 EMS HA Monitors A.03.20        99.715%

cluster10/hermes         +/- 0.5  min MC/ServiceGuard A.10.12 2003231967 EMS HA Monitors A.03.10        99.848%

webserver/apollo         +/- 0.5  min MC/ServiceGuard A.11.09 500776557 EMS HA Monitors A.03.20.01     100.000%

webserver/zeus           +/- 0.5  min MC/ServiceGuard A.11.09 524786597 EMS HA Monitors A.03.20.01     100.000%

************************************************************************************************************************************

=============================================  MC/ServiceGuard Package Event History  ==============================================

Event Date                               Entity                     Class     Downtime     +? P? Notes

===== ================================== ========================== ========= ============ == == ================================

1 Fri Aug 17 00:06:40 CEST 2001      webserver/webserver        package                      Began measurement.

2 Fri Aug 17 00:06:40 CEST 2001      webserver/nfssamba         package                      Began measurement.

3 Fri Aug 17 00:20:40 CEST 2001      webserver/webserver        package                      Measurement terminated.

4 Fri Aug 17 00:20:40 CEST 2001      webserver/nfssamba         package                      Measurement terminated.

5 Fri Aug 17 00:32:22 CEST 2001      webserver/webserver        package                      Began measurement.

6 Fri Aug 17 00:32:22 CEST 2001      webserver/nfssamba         package                +     Began measurement.

7 Thu Aug 23 13:30:10 MDT 2001       cluster10/wsleeper         package                      Began measurement.

8 Thu Aug 23 13:30:10 MDT 2001       cluster10/msleeper         package                      Began measurement.

9 Fri Aug 24 01:20:56 CEST 2001      webserver/webserver        package              1       Down

10 Mon Aug 27 17:23:40 MDT 2001       cluster10/wsleeper         package          44494 +     Down

11 Mon Aug 27 17:23:41 MDT 2001       cluster10/msleeper         package          44494 +     Down

12 Mon Aug 27 17:23:42 MDT 2001       cluster10/FailFast         package                      Began measurement.

13 Mon Aug 27 17:23:42 MDT 2001       cluster10/11XClock.1       package                      Began measurement.

14 Mon Aug 27 17:23:42 MDT 2001       cluster10/sleepingBeauty   package                      Began measurement.

15 Mon Aug 27 17:27:42 MDT 2001       cluster10/FailFast         package              2       Down

16 Tue Aug 28 12:44:13 MDT 2001       cluster10/sleepingBeauty   package              1       Down

17 Tue Aug 28 12:44:23 MDT 2001       cluster10/FailFast         package              2       Down

18 Tue Aug 28 12:44:42 MDT 2001       cluster10/11XClock.1       package              1       Down

19 Thu Aug 30 13:25:43 MDT 2001       cluster10/sleepingBeauty   package              1       Down

20 Thu Aug 30 13:35:43 MDT 2001       cluster10/11XClock.1       package              1       Down

21 Thu Aug 30 13:39:23 MDT 2001       cluster10/11XClock.1       package              6       Down

22 Thu Aug 30 13:39:53 MDT 2001       cluster10/sleepingBeauty   package              6       Down

23 Thu Aug 30 15:04:54 MDT 2001       cluster10/sleepingBeauty   package             13       Down

24 Thu Aug 30 15:17:53 MDT 2001       cluster10/sleepingBeauty   package             21       Down

25 Thu Aug 30 15:39:13 MDT 2001       cluster10/sleepingBeauty   package             74       Down

26 Thu Aug 30 16:33:54 MDT 2001       cluster10/11XClock.1       package              1       Down

27 Thu Aug 30 16:35:23 MDT 2001       cluster10/11XClock.1       package              1       Down

28 Thu Aug 30 17:00:12 MDT 2001       cluster10/11XClock.1       package             19       Down

29 Thu Aug 30 17:00:13 MDT 2001       cluster10/sleepingBeauty   package             20       Down

30 Thu Aug 30 17:17:24 MDT 2001       cluster10/FailFast         package              1       Down

31 Thu Aug 30 17:20:13 MDT 2001       cluster10/sleepingBeauty   package              1       Down

32 Thu Aug 30 17:21:42 MDT 2001       cluster10/11XClock.1       package              1       Down

33 Thu Aug 30 17:25:24 MDT 2001       cluster10/sleepingBeauty   package              1       Down

34 Thu Aug 30 17:44:12 MDT 2001       cluster10/11XClock.1       package              3       Down

35 Thu Aug 30 17:44:13 MDT 2001       cluster10/sleepingBeauty   package          40153 +     Down

36 Wed Sep 05 01:21:25 CEST 2001      webserver/webserver        package              1       Down

37 Sun Sep 09 17:46:42 MDT 2001       cluster10/11XClock.1       package          25751 +     Down

38 Tue Sep 18 11:10:23 MDT 2001       cluster10/FailFast         package              1       Down

39 Tue Sep 18 13:34:34 MDT 2001       cluster10/FailFast         package              1       Down

40 Tue Sep 18 14:07:03 MDT 2001       cluster10/FailFast         package              1       Down

41 Thu Sep 20 01:21:55 CEST 2001      webserver/webserver        package              1       Down

42 Thu Sep 27 13:41:28 MDT 2001       cluster10/FailFast         package              2       Down

43 Thu Sep 27 13:45:13 MDT 2001       cluster10/FailFast         package             72 +     Down

===== ================================== ========================== ========= ============ == == ================================

All times in minutes.  See note at end about rounding.                              + = event ongoing at end of reporting period.

************************************************************************************************************************************

=====================================  Aggregate MC/ServiceGuard Package Availability Report  ======================================

Number of downtime events:                     32

Aggregate measurement time:                 355253

Total downtime:                            155132

MC/ServiceGuard Package availability for the period:   56.332%

************************************************************************************************************************************

======================================  Detailed MC/ServiceGuard Package Availability Report  ======================================

Entity                   Accuracy     Entity info                                                  Availability R?

======================== ============ ============================================================ ============ ==

cluster10/11XClock.1     +/- 0.5  min MC/ServiceGuard A.10.12 2006045407 EMS HA Monitors A.03.20        42.061%

cluster10/FailFast       +/- 0.5  min MC/ServiceGuard A.10.12 2006045407 EMS HA Monitors A.03.20        99.827%

cluster10/msleeper       +/- 0.5  min MC/ServiceGuard A.10.12 2006045407 EMS HA Monitors A.03.20        11.871%

cluster10/sleepingBeauty +/- 0.5  min MC/ServiceGuard A.10.12 2006045407 EMS HA Monitors A.03.20         9.454%

cluster10/wsleeper       +/- 0.5  min MC/ServiceGuard A.10.12 2003231967 EMS HA Monitors A.03.10        11.871%

webserver/nfssamba       +/- 0.5  min MC/ServiceGuard A.11.09 500776557 EMS HA Monitors A.03.20.01     100.000%

webserver/webserver      +/- 0.5  min MC/ServiceGuard A.11.09 524786597 EMS HA Monitors A.03.20.01      99.997%

************************************************************************************************************************************

==========================================================  Error Report  ==========================================================

Entity name                Messages

========================== ====================================================================================================

HP-UX Systems              No errors recorded.

MC/ServiceGuard Clusters   No errors recorded.

MC/ServiceGuard Localnodes No errors recorded.

MC/ServiceGuard Packages   No errors recorded.

************************************************************************************************************************************

=============================================================  Notes  ==============================================================

Rounding:                                                                             Report Fields:

1. In the report history downtime values are rounded to the next higher               Event - The availability event number.

reporting unit (for example, 10 seconds is rounded up to 1 minute).                   Date  - Local time the availability event.

Thus no downtime is ever reported as having a duration of zero.                       Entity - The name of the measured entity.

2. Aggregate values are truncated to the report's significance.                       Class - Entity class under measurement.

For example, 89.9999% is rounded to 89.999% for "5 nines" significance.               Downtime - The duration of downtime.

Thus no availability is ever stated as 100% if there was downtime during              +? - The event is ongoing at report time.

the reporting period.                                                                 P? - Is the event planned (blank if n/a).

3. The aggregate figures are computed using internal precise duration                 Notes - Shutdown cause string if supplied.

measurements.  Thus aggregate figures may not reflect the sum of                      Entity info - Entity-specific information:

duration values as seen in the history section due to rounding.                         system    - Model name, model number,

Aggregate measures should always be used as the preferred measure of                                os name, os revision.

total entity and shop availability.                                                     cluster   - Cluster type, revision, system

id, EMS product, revision.

Accuracy:                                                                                 localnode - Cluster type, revision, system

4. The measurements for entities in this report are constrained by the                              id, EMS product, revision.

polling frequency of the measurement instrument.  For example, if the entity            package   - Cluster type, revision, system

is polled twice a minute, then each downtime period can be in error by as                           id, EMS product, revision.

much as 1 minute (2 * 0.5 minutes, or +/- 0.5 min).  For this reason downtime           Fields may be blank if no data exists.

period values are stated in units no greater than the polling accuracy.               Availability - Entity availability, percent.

5. Each entity is determined to be reachable at the time of report generation.        R? - ? signifies the entity was unreachable

If the system cannot be pinged or otherwise reached from the HA Meter server               at the time of report generation.

the (R?) is set to suspect (?) and the computed availability for that system

may not be meaningful.  The availability of any MC/ServiceGuard element that        Cause Entry Codes:

depends on the unreachable system is also flagged as suspect.                          1. Hardware failure

2. OS failure

Reporting                                                                                3. Application failure

6. Run hamreport -h for complete option details.                                       4. Middleware failure

7. The results generated by this report are current to the time of the report.         5. Patch/Software installation

A later run of the report may produce different results because the entities           6. Kernel reconfiguration

under measurement have been measured for that much longer.  In addition,               7. Hardware upgrade/installation

systems that were previously unreachable may now be reachable and their                8. Hardware reconfiguration

availability data may consequently be more accurate.                                   9. Scheduled reboot

8. Error messages indicating problems in collecting HA Meter data may                 10. Other scheduled maintenance

appear in the Error Report.  Such messages appear only so long as the                 11. System backup

problem persists.                                                                     12. Environment Failure

9. The Event History reports may contain no data.  This would happen if the           13. Enter cause

entity experienced no availability events during the report's query period,

in which case the entity was up, down, or unmeasured during the period.